STEP-BY-STEP GUIDE

Group Remote Control

Configuration & Operation

Adani Mumbai · Sewage Treatment Plant

Version 1.0 · 18 June 2026

# About this guide

This guide is split into two independent walkthroughs:

- Part A — Configuring a group (software side). For the implementer / commissioning engineer who is bringing a new group online.

- Part B — Using Group Remote Control (operator side). For the operator who needs to start, stop, or hand control of a group back to the PLC.

Each part is self-contained — read only the one that applies to your task.

# Part A · Configuring a group

A group is the named collection of equipment that the operator will later start, stop, or place into standby together. Configuring a group is a three-step workflow: name it, associate the equipment that belongs to it, and confirm.

Before you start  You need an implementer account and the list of equipment IDs that will participate in the new group. Equipment must already exist in the platform's catalog.

STEP 1    Create the group

1.  Open the configuration screen from the page selector.

2.  Click + Create group in the top-right of the screen.

3.  A centered modal opens. Enter the following:

  - Group Name — required. A short, operator-facing label (for example, “Adani SBR Group”, “PSF Train 1”, “RO Skid B”).

  - Description — optional. One line that explains what the group does or when it runs.

4.  Click Save group. The modal closes and the new group appears as a card at the top of the configuration stack, auto-expanded so you can move to Step 2 immediately.

Naming guidance  Use a name the operator will recognise in a stressful situation. Avoid internal codes — pick a name that matches what is written on the panel or the SOP.

STEP 2    Associate equipment with the group

With the group card expanded, find the Equipment section.

1.  Click into the search box labelled “Type to search and add equipment…”.

2.  Start typing. The list filters live — by name and by equipment ID.

3.  Click any suggestion. The equipment instantly appears as a chip below the search box. The search box clears and is ready for the next entry.

4.  Repeat until every piece of equipment that should respond to this group's commands is listed.

5.  Removing equipment — click the × on any chip to detach that equipment from the group. There is no confirmation prompt; the change is immediate and reversible.

Equipment can belong to more than one group  Re-using the same pump or blower across multiple groups is allowed. The platform reconciles overlapping commands using the interlock rules already configured in the PLC.

STEP 3    Review and finish

1.  Scan the card header — it should show the correct equipment count and group name.

2.  Click the chevron on the card header to collapse it. The card now lives in the configuration stack alongside any others you have created.

3.  The group is now visible to the operator. They will see it in the Group Control panel on the plant layout the next time they refresh that view.

## Managing groups after creation

| Action | Where | What happens |
| --- | --- | --- |
| Rename or update description | Pencil icon on the group card header | Opens the same modal with current values pre-filled. |
| Add equipment | Search box inside the expanded card | Same live autocomplete as during creation. |
| Remove equipment | × on the equipment chip | Equipment detaches immediately; no confirm. |
| Delete the group | Bin icon on the group card header | Asks to confirm. Equipment is unaffected — only the group definition is removed. |
| Search across groups | Search bar at the top of the page | Filters by group name, description, and equipment names. |

Validation  Group name is required and cannot be empty. Two groups can share a name, but a warning will appear if you try to save a duplicate. There is no enforced minimum equipment count — an empty group is allowed (operators just see “0 equipment” on it).

# Part B · Using Group Remote Control

Group Remote Control lets you start, stop, or place an entire group of equipment into standby with one action — without overriding the PLC's safety logic. Use it when you need to bring a train, skid, or section up or down as one.

When to use this  Group control is for coordinated operations — e.g. bringing the SBR train online for the morning shift. For routine threshold tuning of a single set point, use the Unit Processes drawer instead.

## B.1  Opening the Group Control panel

1.  On the Plant Layout, click the Group Control button in the top navigation.

2.  The Group Control side panel slides in from the right. It is labelled with the group's name (e.g. “Adani SBR Group”) and the live equipment count.

3.  If you have more than one group configured, use the group selector at the top of the panel to switch between them.

## B.2  Reading the Group Mode card

The top card of the panel — Group Mode — shows whether the group is currently under remote control or running locally on the PLC.

| Status | Meaning | What you can do |
| --- | --- | --- |
| Local | PLC is running the group autonomously based on its automation logic. | Read-only. Switch to Remote to take control. |
| Remote | Group is accepting commands from this software. | Start / Stop / Standby the group; control individual equipment below. |
| Unavailable | Remote link is not negotiated, or the group has no equipment configured. | Click Refresh status. If the message persists, escalate to the controls engineer. |

### Switching from Local to Remote

1.  Click Request Remote Control. A technical loader appears showing the link negotiation with the PLC.

2.  The loader runs to completion (typically 3–5 seconds). On success, Group Mode flips to Remote and the action buttons become active.

3.  If negotiation fails, the loader reports the failure reason. The group stays in Local. Retry, or escalate if the failure is persistent.

## B.3  Group-level actions

Once Group Mode is Remote, four group-level actions are available.

- Start group — commands every equipment in the group to its running state, in the order defined by the PLC's startup sequence. Interlocks are respected.

- Stop group — commands every equipment to stop, again in PLC-defined order.

- Standby — leaves equipment energised but holds it in a safe idle (for example, pumps stay primed but do not run).

- Refresh status — re-reads the PLC. Use this if a panel field looks stale.

Interlocks are never bypassed  Group commands are sent equipment-by-equipment in PLC-defined order. If an interlock blocks a piece of equipment, that equipment does not move and the panel reports it inline. The group action does not “fail” as a whole — partial state is shown and you can retry the blocked items individually.

## B.4  Controlling individual equipment inside the group

Below Group Mode is the Equipments card. Each row shows one equipment with its live status and direct controls.

1.  Find the equipment in the list. Each row shows the equipment name, its type (pump, blower, valve…), and its current state (Running, Stopped, Standby, Fault).

2.  Use the inline action buttons to drive that single equipment. Available actions vary by equipment type:

  - Pumps and blowers — Start, Stop, Standby.

  - Valves — Open, Close.

  - VFD-driven equipment — Set output (opens a small step input).

3.  Every individual action respects the same interlocks as group-level actions. If an interlock blocks a command, the affected row shows an interlock badge with the reason (e.g. “Upstream valve closed”).

## B.5  Releasing remote control back to the PLC

When you are done with remote control of a group, hand control back so the PLC's automation can resume.

1.  On the Group Mode card, click Release to Local.

2.  Optionally, set a delayed release — for example, “return to Local in 30 minutes.” The panel will show a countdown and switch back automatically when it elapses.

3.  Confirm the release. The Group Mode flips back to Local; all action buttons are disabled.

Auto-release safety net  If the platform loses its link to this software for more than 5 minutes, the PLC automatically returns the group to Local on its own. This is a safety feature — you can rely on it, but the right habit is to release manually when you finish.

## B.6  Audit and logging

Every group-level and individual-equipment action is logged. The audit entry contains:

{ ts, user_id, group, equipment_id?, action, before, after, link_status, note? }

Group-level commands produce one parent entry plus one child entry per equipment that received a command, so the audit viewer can collapse or expand the change set.

# Quick reference

| I want to… | Go to | Tap |
| --- | --- | --- |
| Create a new group | Configuration screen | + Create group → name → Save |
| Add equipment to a group | Group card → expanded | Search box → click suggestion |
| Rename a group | Group card header | Pencil icon |
| Delete a group | Group card header | Bin icon → confirm |
| Take a group on Remote | Plant Layout → Group Control panel | Request Remote Control |
| Start the whole group | Group Control panel → Group Mode | Start group (Remote only) |
| Control one equipment in a group | Group Control panel → Equipments | Inline action on that row |
| Hand control back to PLC | Group Control panel → Group Mode | Release to Local |

# Glossary

| Term | Definition |
| --- | --- |
| Group | A named collection of equipment that can be commanded together from this software. |
| Group Mode | Whether the group is currently under PLC control (Local) or this software's control (Remote). |
| Interlock | A safety rule on the PLC that prevents one equipment from running unless the conditions around it are met. |
| Local | PLC is running the group autonomously. This software can read state but cannot send commands. |
| Remote | This software has the right to send commands to the group. Interlocks still apply. |
| Standby | Safe-idle state — equipment is energised but not running. Faster to bring back online than from Stopped. |
| Release to Local | The act of explicitly returning control of a group to the PLC's automation. |
| Auto-release | PLC's safety mechanism that returns a group to Local if the software link is lost for more than 5 minutes. |