Digital Paani

Set Points

Developer Documentation

Audience: developers implementing set-point configuration and runtime behaviour. Last updated: with the addition of the Transfer Pump Set Point type and the standalone Set Point Configuration screen.

# 1. What is a set point?

A set point is a numeric threshold or target value stored on the PLC that drives equipment behaviour (start / stop / dose / open / close / VFD output). The PLC’s automation logic is fixed — only the threshold values are overwritten by operators through this software.

Every set point has an HMI Tag that maps 1:1 to a PLC tag. Tags are auto-generated by the configuration UI (read-only); the PLC integration team maps each auto-generated tag to the actual PLC tag during plant commissioning.

# 2. Common fields (every type)

Every set point — regardless of type — captures the following at configuration time:

| Field | Type | Required | Notes |
| --- | --- | --- | --- |
| Set Point Type | enum | ✓ | One of the 9 types in §3 |
| Set Point Name | string | ✓ | Operator-facing label (e.g. CASS Basin 1 high level cut-in) |
| Set Point Description | text | optional | When the set point fires, what equipment behaviour it drives |
| Set Point Min (safe min) | number | ✓ | Floor of the allowed override range. Values below trigger a soft warning |
| Set Point Max (safe max) | number | ✓ | Ceiling. Values above trigger a soft warning |
| HMI Set Point Tag | string | auto | Generated from <UP_NAME>.<TYPE>[_<ROLE>]_<NN>_SP. Read-only in UI |
| Linked Unit Process | reference | optional | The unit process this set point belongs to (drives Dashboard grouping) |

## Validation (server + client)

- Min < Max — always.

- Current (the live set point value the PLC reads) must satisfy Min ≤ Current ≤ Max.

- Name is non-empty and trimmed.

- HMI Tag uniqueness is enforced when persisting (auto-generation already keeps uniqueness via the _NN suffix).

## Override semantics

- The system never blocks an operator setpoint change.

- If the operator’s new value falls outside [Min, Max], a warning modal opens and an explicit override is required.

- Every change (in-range or override) is logged: old → new, user_id, timestamp, hmi_tag, note.

# 3. Set point types & their config questions

Each row below describes what to ask the implementer at configuration time.

### 3.1 Level

- Inputs: one reading

- Unit: %

- Safe range: Min, Max

- Purpose: Tank level threshold (e.g. "transfer pump starts at 70%")

### 3.2 DO (Dissolved Oxygen)

- Inputs: one reading

- Unit: mg/L

- Safe range: Min, Max

- Purpose: Drives blower ON/OFF and VFD output (RPM / Hz / current)

### 3.3 Differential Pressure

- Inputs: one reading

- Unit: bar

- Safe range: Min, Max

- Purpose: Triggers backwash sequence (valves ON/OFF)

### 3.4 pH

- Inputs: one reading

- Unit: pH (dimensionless 0–14)

- Safe range: Min, Max

- Purpose: Triggers dosing pumps (NaOH / HCl)

### 3.5 FRC (Free Residual Chlorine)

- Inputs: one reading

- Unit: ppm (or mg/L)

- Safe range: Min, Max

- Purpose: Triggers NaOCl dosing pump

### 3.6 ORP (Oxidation-Reduction Potential)

- Inputs: one reading

- Unit: mV

- Safe range: Min, Max

- Purpose: Triggers ORP-correction dosing

Values commonly negative for anoxic processes.

### 3.7 Flow

- Inputs: one reading

- Unit: m³/hr

- Safe range: Min, Max

- Purpose: Changes VFD output of permeate / feed pumps (no ON/OFF toggle)

### 3.8 Time

- Inputs: one reading

- Unit: minutes (default) — also seconds and hours

- Safe range: Min, Max

- Purpose: Backwash duration, decant duration, fill duration, etc.

### 3.9 Transfer Pump Set Point  ★ special case

A Transfer Pump Set Point is logically one set point that physically resolves to four HMI tags (and four PLC writes). It controls a pump that moves liquid from a source tank to a destination tank.

### Inputs

| Sub-field | What | Each has its own |
| --- | --- | --- |
| Source Tank Start Level | Level above which pump starts | min, max (safe range) |
| Source Tank Stop Level | Level at/below which pump stops | min, max |
| Destination Tank Start Level | Level above which transfer holds | min, max |
| Destination Tank Stop Level | Level at/below which transfer resumes | min, max |

All four are in %.

### Validation

- Per-tank ordering: Source Start ≤ Source Stop, Destination Start ≤ Destination Stop.

- Per-sub-setpoint safe ranges: min ≤ current ≤ max for each of the four values independently.

- Min < Max on each sub-setpoint’s safe range.

### HMI Tag generation

A single Transfer Pump set point produces four tags (one per sub-role):

<UP_NAME>.LT_SOURCEMIN_<NN>_SP    ← Source Start

<UP_NAME>.LT_SOURCEMAX_<NN+1>_SP  ← Source Stop

<UP_NAME>.LT_DESTMIN_<NN+2>_SP    ← Destination Start

<UP_NAME>.LT_DESTMAX_<NN+3>_SP    ← Destination Stop

Internally we tag the four set-point records with a shared `groupId` and `groupName` so the UI can re-aggregate them into one row in the Configuration screen and one card in the operator drawer/dashboard.

### Operator behaviour

- The operator edits all four values in one form (single "Edit" action → 4 inputs → Save → 4 PLC writes).

- The Dashboard renders them as one card showing both ranges at a glance.

- Audit log writes a single grouped entry referencing all four old → new pairs.